## Slide 1: Getting Started with EPICS Lecture Series
Introductory Session II
John Maclean
8/16/04
Notes: 07/30/26
Test
<number>

## Slide 2: Overview
<number>
Lay the foundation for understanding an EPICS control system
Introduce IOCs
  Channel Access (CA)
  Database
  Sequencer
  Device Support
Choosing the correct tools for the job
  When to use a database
  The sequencer, what is it good for?
  Why write your own CA client program?
How fast is EPICS?
How to find more information
  Website walk through
Virtual LINAC installation
Notes: 07/30/26
Test
<number>

## Slide 3: Canonical Form of an EPICS Control System
<number>
Commercial Instruments
IOC
IOC
IOC
IOC
CAS
CAS
Channel Access
IOC Software
EPICS Database
Sequence Programs
Custom Programs
Real-time
Control
Client Software
MEDM
ALH
StripTool
TCL/TK
Perl Scripts
OAG Apps
Many, many others
CA Server Application
Custom Chassis/Panels
Technical Equipment
Process Variables

## Slide 4: Introducing the IOC
<number>
Input Output Controller
A computer running software called “IOC Core”
The computer can be:
  VME based, running vxWorks (only choice until Release 3.14) or RTEMS
  PC running Windows, Linux, RTEMS
  Apple running OSX
  UNIX Workstation running Solaris
Usually has Input and/or Output devices attached
An EPICS control system must consist of at least one Channel Access Server (usually an IOC)
An IOC has one or more databases loaded. The database tells it what to do
Notes: 07/30/26
Test
<number>

## Slide 5: Inside an IOC
<number>
LAN
I/O Hardware
IOC
The major software components of an IOC (IOC Core)
Database
Sequencer
Device Support
Channel Access
Notes: 07/30/26
Test
<number>

## Slide 6: Channel Access
<number>
Allows other programs (CA Clients) to see and change values of Process Variables in an IOC (CA Server)
CA Clients may
  Put (write)
  Get (read)
  Monitor
  data of Process Variables
IOCs are both CA clients and CA servers. They can interact with data in other IOCs
A CA Client can connect to many servers
A CA Server may serve many clients
A very efficient an reliable protocol
CA Client
CA Server
Workstation
IOC
Network

## Slide 7: Inside an IOC
<number>
Channel Access
LAN
Sequencer
Device Support
I/O Hardware
IOC
The major software components of an IOC (IOC Core)
Database
Notes: 07/30/26
Test
<number>

## Slide 8: EPICS Databases – What are they for?
<number>
Interface to process instrumentation
Distribute processing
Provide external access to all process information
Use common, proven, objects (records) to collect, process and distribute data
Provide a common toolkit for creating applications
Notes: 07/30/26
Test
<number>

## Slide 9: What are records?
<number>
A record is an object with
  A unique name
  Properties (fields) that contain information (data)
  The ability to perform actions on that data
A personnel record in a relational database has a name, and fields containing data
XYZ1234
Employee: James Bond
Badge # : 007
Address : Whitehall, London
Salary : £70070.07
Unique record name
Fields
Data
Notes: 07/30/26
Test
<number>

## Slide 10: What are EPICS records?
<number>
A record is an object with…
  A unique name e.g. S28:waterPressure
  Controllable properties (fields) e.g. EGU
  A behavior - defined by its record type
  Optional associated hardware I/O (device support)
  Links to other records
Each field can be accessed individually by name
A record name and field name combined give a the name of a process variable (PV)
A Process Variable name is what Channel Access needs to access data
Notes: 07/30/26
Test
<number>

## Slide 11: A Process Variable name
<number>
A PV name is comprised of two parts
  The record name, and
  A the name of a field belonging to that record
For example…
A record name
L1:water:temperature
A field name
EGU
.
A dot to join them
A Process variable name
Note that if no field name is given, Channel Access will default to using the .VAL field
i.e. to CA, “L1:water:temperature” = “L1:water:temperature.VAL”

## Slide 12: What do records do?
<number>
Records are active, they do things
  Get data from other records or from hardware
  Perform calculations
  Check values are in range and raise alarms
  Put data to other records or to hardware
  Activate or disable other records
  Wait for hardware signals (interrupts)
What a record does depends upon its type and the values in its fields
A wide range of records have already been created
New record types can be added to a new application as needed
A record does nothing until it is processed
Notes: 07/30/26
Test
<number>

## Slide 13: Record types
<number>
Classified into four general types
Input: e.g.
  Analog In (AI)
  Binary In (BI)
  String In (SI)
Algorithm/control: e.g.
  Calculation (CALC)
  Subroutine (SUB)
Output: e.g.
  Analog Out (AO)
  Binary Out (BO)
Custom: e.g.
  Beam Position Monitor
  Multi Channel Analyzer
Notes: 07/30/26
Test
<number>

## Slide 14: Some record types
<number>
Analog in
Analog out
Binary in
Binary out
Calculation
Calculation out
Compression
Data fanout
Event
Fanout
Histogram
Motor
Multi bit binary input
Multi bit binary output
PID control
Pulse counter
Pulse delay
Scan
Select
Sequence
String in
String out
Subarray
Subroutine
Waveform

## Slide 15: Graphical view of a record
<number>
Notes: 07/30/26
Test
<number>

## Slide 16: IOC view of a record
<number>
field(DRVH,"100")
field(DRVL,"0")
field(HOPR,"80")
field(LOPR,"10")
field(HIHI,"0.0e+00")
field(LOLO,"0.0e+00")
field(HIGH,"0.0e+00")
field(LOW,"0.0e+00")
field(HHSV,"NO_ALARM")
field(LLSV,"NO_ALARM")
field(HSV,"NO_ALARM")
field(LSV,"NO_ALARM")
field(HYST,"0.0e+00")
field(ADEL,"0.0e+00")
field(MDEL,"0.0e+00")
field(SIOL,"")
field(SIML,"")
field(SIMS,"NO_ALARM")
field(IVOA,"Continue normally")
field(IVOV,"0.0e+00")
}
record(ao,"DemandTemp") {
field(DESC,"Temperature")
field(ASG,"")
field(SCAN,"Passive")
field(PINI,"NO")
field(PHAS,"0")
field(EVNT,"0")
field(DTYP,"VMIC 4100")
field(DISV,"1")
field(SDIS,"")
field(DISS,"NO_ALARM")
field(PRIO,"LOW")
field(FLNK,"")
field(OUT,"#C0 S0")
field(OROC,"0.0e+00")
field(DOL,"")
field(OMSL,"supervisory")
field(OIF,"Full")
field(PREC,"1")
field(LINR,"NO CONVERSION")
field(EGUF,"100")
field(EGUL,"0")
field(EGU,"Celcius")
Notes: 07/30/26
Test
<number>

## Slide 17: EPICS Databases – What are they?
<number>
A collection of one or more EPICS records of various types
Records can be interconnected and are used as building blocks to create applications
A data file that’s loaded into IOC memory at boot time
Channel access talks to the IOC memory copy of the database
Notes: 07/30/26
Test
<number>

## Slide 18: Our First Database
<number>
Analog In
ProcTemp
EGU : deg C
VAL
INP
Temperature Sensor
IOC
Database
Analog to Digital Converter
0 – 100°C
0 – 10V
8 bit ADC
0 – 10V
0 – 255 bits
EGUL: 0
EGUF: 100
HIGH: 51
Process
45.5°C
4.55V
116 bits
Channel Access Server
Normal Operation
5 - 50°C
Channel Access Client
Tell me about ProcTemp
ProcTemp
.VAL = 45.5
.EGU = deg C
.STAT = Normal
45.5 deg C
51.5°C
5.15V
132 bits
51.5 deg C
ProcTemp
.VAL = 51.5
.EGU = deg C
.STAT = MAJOR

## Slide 19: Record Processing
<number>
Record processing can be periodic or event driven
Periodic: Standard scan rates are…
  10, 5, 2, 1, 0.5, 0.2 and 0.1 seconds
  Custom scan rates can be configured up to speeds allowed by operating system and hardware
Event driven: Events include
  Hardware interrupts
  Request from another record via links
  EPICS Events
  Channel Access Puts
Notes: 07/30/26
Test
<number>

## Slide 20: Database Processing
<number>
Problem:
In the LINAC we have a water chiller that must be turned ON whenever the average temperature of two temperature sensors rises above a set point. The set point is nominally 10 degrees centigrade.
Binary out
L1:water:chillerCtl
Calculation
L1:water:tempChk
CALC: ( (A+B)/2 ) > C
C: 10
SCAN: 10 second
Analog In
L1:water:temp1
EGU: deg C
VAL
INP
EGU: deg C
VAL
INP
INPB
INPA
VAL
DOL
OUT
T2
Sensor
Sensor
T1
IOC
Database
ADC
ADC
Binary I/O
Chiller
Analog In
L1:water:temp2
Notes: 07/30/26
Test
<number>

## Slide 21: Inside an IOC
<number>
Channel Access
LAN
Device Support
I/O Hardware
IOC
The major software components of an IOC (IOC Core)
Database
Sequencer
Notes: 07/30/26
Test
<number>

## Slide 22: The Sequencer
<number>
Runs programs written in State Notation Language (SNL)
SNL is a ‘C’ like language to facilitate programming of sequential operations
Fast execution - compiled code
Programming interface to extend EPICS in the real-time environment
Common uses
  Provide automated start-up sequences like vacuum or RF where subsystems need coordination
  Provide fault recovery or transition to a safe state
  Provide automatic calibration of equipment
Notes: 07/30/26
Test
<number>

## Slide 23: SNL implements State Transition Diagrams
<number>
State A
State B
Event
Action
Transition
A to B

## Slide 24: STD Example
<number>
Start
Low vacuum
High vacuum
pressure > 5.1 uTorr
Open the valve
pressure < 4.9 uTorr
Close the valve

## Slide 25: Inside an IOC
<number>
Channel Access
LAN
I/O Hardware
IOC
The major software components of an IOC (IOC Core)
Database
Sequencer
Device Support
Notes: 07/30/26
Test
<number>

## Slide 26: Device Support
<number>
Device and driver support interface hardware to the database
Examples of devices….
VME cards: ADC, DAC, Binary I/O e.t.c.
Motor controllers
Oscilloscopes
PLCs

## Slide 27: Device Support
<number>
Usually has to be written for ‘new’ hardware
Good news – someone, somewhere has usually written support for your device, or a very similar one before
See the EPICS web site for available support
Or ask the EPICS community

## Slide 28: When to use databases
<number>
Hardware connection
Real time performance – no network latencies
Whenever a database is good enough
Advantages | Disadvantages
Simplify hardware connection | If you have device support
Configuring not programming. | You need to understand database use
Database is easily understood by other EPICS developers | 
Speed - All processing (often) in same machine | 

## Slide 29: When to use the sequencer
<number>
For sequencing complex events
E.g. Parking and unparking a telescope mirror
Photograph courtesy of the Gemini Telescopes project

## Slide 30: When to use clients
<number>
To interact with the control system
Many already exist – MEDM, ALH, Strip Tool, archiver etc.
For data analysis or visualization
Supervisory control
E.g. to manage an accelerator

## Slide 31: How fast is EPICS?
<number>
Can be fast or slow, it depends how you use it!
Use the correct tool for the job; Database, sequencer, custom code (ioc) or custom code (client)
Ultimately speed depends upon hardware
Some benchmarks*:
Machine | OS | CPU | Speed | Rec/sec | %CPU
MVME167 | vxWorks | 68040 | 33MHz | 6000 | 50
MVME 2306 | vxWorks | PPC604 | 300MHz | 10000 | 10
MVME5100 | vxWorks | PPC750 | 450MHz | 40000** | 10**
PC | Linux | PII | 233MHz | 10000 | 27
PC | Linux | P4 | 2.4GHz | 50000 | 9
Database design and periodic scanning effect apparent system speed
*Benchmark figures courtesy of Steve Hunt (PSI)
**Extrapolated from performance figures provided by L.Hoff, BNL

## Slide 32: Apparent performance
<number>
Binary out
L1:water:chillerCtl
Calculation
L1:water:tempChk
CALC: ( (A+B)/2 ) > C
C: 10
SCAN: 10 second
Analog In
L1:water:temp1
EGU: deg C
VAL
INP
EGU: deg C
VAL
INP
INPB
INPA
VAL
DOL
OUT
IOC
Database
ADC
ADC
Binary I/O
Actuator
Chiller
Analog In
L1:water:temp2
T2
Sensor
Sensor
T1
C: 15
SCAN: 10 second
C: 10
14°C
12°C
Process Now
Process Now
Process Now
12
14
1
ON
0
OFF

## Slide 33: The EPICS web site
<number>
The central site for EPICS information
Documentation
CA Clients
Device support
Tech-talk
http://www.aps.anl.gov/epics

## Slide 34: Installing the virtual LINAC
<number>
Linux, Solaris, Mac OSX
  Insert the CD
  Mount the CD (if it’s not automounted)
  Run the setup.sh script from the CD
        ‘cd’ to your install directory
        Run ‘start.sh’ to start both medm and the virtual LINAC IOC
        Or start things individually using the scripts provided

## Slide 35: Installing the virtual LINAC - Windows
<number>
Note: You will need Exceed V7.0 or later installed
  Insert the CD
  If autorun is enabled you will see a screen with instructions, if not open ‘WIN32/README.HTM’ (on the CD) in your browser
  Run ‘MEDM Virtual Linac’ to start the MEDM screen
  Run ‘Start Virtual Linac’ to start the virtual LINAC IOC
  Install the Extensions by running ‘WIN32/EPICSEX39ISETUP.EXE’ from the CD
  Install the Virtual LINAC by executing ‘WIN32/VIRTUALLINACSETUP.EXE’ from the CD
  Program icons will appear on the desktop and start menu

## Slide 36: If You Don’t Have the CD
<number>
The CD image and individual OS versions can be obtained from http://www.aps.anl.gov/epics/download/examples/index.php
Remember, the CD image is an image file. You may need to use a command such as “Create CD from image file” on your Windows CD creation program

## Slide 37: Review
<number>
Input Output Controllers are a fundamental part of an EPICS control system
The database is the primary means of telling an IOC what to do
An EPICS database is composed of records configured to perform an application
Channel Access is a means for other computers to communicate with record fields
Sequencer programs can be used to sequence complex operations
Device support software allows records to interact with hardware inputs and outputs
EPICS is fast and efficient but can appear slow if used without consideration

## Slide 38: Acknowledgements
<number>
Andrew Johnson (APS-Controls)
Bob Dalesio (LANL)
Deb Kerstiens (LANL)
Rozelle Wright (LANL)